REQUEST FOR QUOTATION
SPECIFICATION OF STANDARD GOODS

Procurement No: 27-G001-22

## Specification

Refer to the Technical and Specification Requirement section.

### Background

The project is funded by International Solar Alliance and Implemented by the Ministry of Infrastructure and Sustainable Energy through its Energy Planning Unit. The project is focus on introducing an off grid solar power system to Nawai Junior Secondary School, Tamana Island and aims to up lift the education standard at the junior level. Therefore, the tender objectives are to provide the following:

- 1 x set of 5kW off grid PV solar systems for Nawai Junior Secondary School, Tamana Island

### Requirements

- All supporting documentation must be in English.

- Tax clearance letter

- Delivery time schedule

- Bank Statement

- Valid Business licence

- Financial Proposal

- Technical Proposal

### Installation services

The supplier should provide necessary installation documents such as:

      - Design Diagram

      - Manuals:

- Installation

- Configuration

- Reference

### Delivery Time

| No. | Description of Goods |  | Quantity | Unit Price | Total Price at final destination | Delivery Date |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 5kW (Complete Set) |  | 1 |  |  | Max 6 weeks from Contract signature |
| 2 | Freight |  | LS |  |  |  |
|  |  | TOTAL |  |  |  |  |

## Description of the Goods

- 1 complete set of 5kW Solar off Grid power system for Nawai Junior Secondary School, Tamana Island. The system is a single-phase system.

| TECHNICAL REQUIREMENT and SPECIFICATIONS FOR TENDER – SOLAR PV GRID FOR RURAL CHURCHES MAKIN KUC AND TAMANA KPC Churches. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Specifications Required | Specifications Offered | Notes, Remarks, References | Evaluation |
|  |  |  |  | Committee Notes |
| 1 | General Requirements |  |  |  |
|  | The Solar mini-grid project under this Terms of Reference (TOR) must include but not necessarily be limited to the following job activities; |  |  |  |
| 1.1 | Design a Standalone Solar Systems with Generator Backup to be installed by Kiribati Ministry of Infrastructure and Sustainable Energy to supply power to the site identified. The Solar PV unit must continuously supply 240 V AC, 50Hz balanced sine wave electricity to the mini-grid systems. The Solar PV unit shall be of the modular type to allow for further expansion of the installed capacity. The following are various capacity listed below. - 1 x 5kW complete set off grid pv solar system. |  |  |  |
| 1.2 | Supply of Major System Components for the system in clause (I) above. |  |  |  |
| 1.3 | Provide skills training to Kiribati |  |  |  |
|  | Ministry of Infrastructure and Sustainable Energy technical staff during installation of the Solar System |  |  |  |

| 1.4 | Design should incorporate single phase diesel generator for use as back up. Design should aim to reduce the run time of the generator to a minimum to reduce fuel costs and CO2 emissions. |  |  |  |
| --- | --- | --- | --- | --- |
| 1.5 | All wiring and system designs must conform to Australia & New Zealand standards. |  |  |  |
| 1.6 | System Performance Figures as per item 3.0 |  |  |  |
| 2 | Photovoltaic System |  |  |  |
| 2.1 | General terms and conditions where the PV Arrays will be installed include. 1. A Minimum Array Size of 5kWp. |  |  |  |
| 2.2 | Suitable for an environment of high ambient temperature, high humidity and high level of atmospheric salt. |  |  |  |

| 2.3 | The system must be designed to suit tropical costal conditions. All system components are to be fully integrated and compatible |  |  |  |
| --- | --- | --- | --- | --- |
| 2.4 | Area occupied by PV Array installation must be minimized as much as possible |  |  |  |
| 2.5 | The required module shall have a manufacturing warranty of 10 years and a performance warranty of 25 years |  |  |  |
| 3 | Photovoltaic Support Structure (Rack) |  |  |  |
| 3.1 | PV modules need to be supported on a suitable On-roof Mounted support Structure for Nawai JSS shall use on-roof mounted form that could withstand corrosive |  |  |  |
| 3.2 | The material of rack and mounting brackets of the solar arrays must be designed to withstand corrosive maritime climate and strong winds in access of 150km/hour. All support structure components including brackets and fasteners must be able to resist at least 15 years of outdoor exposure without any appreciable corrosion |  |  |  |
| 3.3 | Tilt angle shall be adjustable between 10-30 degrees and suitable to the design of system as outlined in item 3.0 |  |  |  |
| 3.4 | A manual containing construction and assembly of the mounting structures and mounting of modules must be provided with tender |  |  |  |

| 3.5 | The aluminum rails shall be of a 6005-T5 aluminum alloy and have an ultimate tensile strength of 19.9kN/m². The rail must have the section modulus of 5.78cm3 or larger. All bolts and screws will be made of stainless steel (316SS). All clamps that attach directly to the roof should be S-5 brand or approved equal with proper roof sealant at clamp to roof connection. All exposed materials shall be non-toxic to allow for collection of potable rainwater |  |  |  |
| --- | --- | --- | --- | --- |
| 3.6 | Engineering Diagrams for foundations and Framing should be supplied with tender |  |  |  |
| 4 | Battery Bank |  |  |  |
| 4.1 | A battery bank design shall meet the daily depth of discharge to meet the daily watt hour requirement of the site and can continue supply the load for at least 3 autonomous days to a DOD of 70%. |  |  |  |
| 4.2 | Batteries shall be Lithium-ion battery cells 48V 24kWh. |  |  |  |
| 4.3 | Battery designs shall have no more than 48V (6 x 4kWh) series. |  |  |  |
| 4.4 | Batteries should have a life expectancy of 8 years or more |  |  |  |
| 4.5 | Battery design specified should be OPzV or OPzS |  |  |  |
| 4.6 | The batteries shall be designed to operate in a tropical, marine environment subject to intermittent salt spray, continuous exposure to high ambient temperature (25-35 °C) and humidity approaching 100%. |  |  |  |
| 4.7 | Battery bank voltage shall be 48V nominal voltage |  |  |  |

| 4.8 | Tenderers must include a statement of warranties in effect, including what specifically is covered under warranty and requirements for obtaining compensation for batteries which have failed under warranty |  |  |  |
| --- | --- | --- | --- | --- |
| 5 | Solar Inverters |  |  |  |
|  | The Solar Inverters required for the project should meet the following requirements using SMA Inverters. |  |  |  |
| 5.1 | Minimum Capacity of 5 kWp |  |  |  |
| 5.2 | Be able to supply Single phase 240 V Power to the micro grid |  |  |  |
| 5.3 | 2 independent MPPT inputs |  |  |  |
| 5.4 | 3 strings per MPP input |  |  |  |
| 5.5 | Minimum efficiency of 98 % |  |  |  |
| 5.6 | Integrated monitoring and management features |  |  |  |
| 5.7 | IP 65 Rating |  |  |  |
| 5.8 | The inverter shall be labeled with the following information · Manufacturer; · Serial number; · Nominal output power at 15°C; · Manufacturing date; |  |  |  |
|  | · Country of origin; · Clear indication of the positive and negative connection on the battery cable; · Safety warnings as needed. |  |  |  |

| 5.9 | Tenderers must include a statement of warranties in effect, including what specifically is covered under warranty and requirements for obtaining compensation for inverters which have failed under warranty. If as a result of the failure of one inverter (or any related equipment) the inverter is not available for a period of longer than three (3) consecutive days the warranty period shall be extended for that period of non-availability. |  |  |  |
| --- | --- | --- | --- | --- |
| 6 | Battery Inverter/Chargers |  |  |  |
|  | A bi-directional inverter/Charger system with input voltage of 48VDC |  |  |  |
| 6.1 | Output of single phase 240V AC at 50Hz |  |  |  |
| 6.2 | Pure sine wave |  |  |  |
| 6.3 | Minimum IP 54 Enclosure |  |  |  |
| 6.4 | Minimum of 50 Amp internal transfer switch for generator connection |  |  |  |
| 6.5 | Integrated 2 wire Generator Control |  |  |  |
| 6.6 | Load Shedding Control Capability |  |  |  |
| 7 | Other Components |  |  |  |
|  | Other components include but not limited to; |  |  |  |

| 7.1 | Salt Resistant DC Junction Box containing DC circuit breaker, Isolating fuses/circuit breakers for DC inputs from all strings of the solar array, Isolating circuit breakers from inverters/charge controllers, positive and negative buses for the termination of all dc sources |  |  |  |
| --- | --- | --- | --- | --- |
| 7.2 | Salt Resistant AC Junction Box with all integrated Circuitry and fusing for connection of solar inverters, Battery Inverters Generator and Load |  |  |  |
| 7.3 | AC Load Shedding Contactors |  |  |  |
| 7.4 | All Battery Cabling and Fusing |  |  |  |
| 7.5 | Cables for DC and AC circuit from; a. PV array to DC Junction Box b. DC Junction Box to Solar Inverters. c. Solar inverters to AC Junction box d. AC Junction Box to Battery Inverters e. Battery inverters to battery bank and cell interconnects |  |  |  |
| 7.6 | Web based Data Logger/ Metering |  |  |  |
| 7.7 | Installation Tools and components: (Not required) |  |  |  |

| 7.8 | Civil work materials for on-roof mount installation |  |  |  |
| --- | --- | --- | --- | --- |
| 8 | Services As part of the tender the Kiribati Ministry of Infrastructure and Sustainable Energy requires a daily schedule of rates from the contractor for the following Services. |  |  |  |