Kiribati

Request for Proposal

Prepay Electricity Meters &

Associated Services

Appendix A: Technical Requirements & Response Templates

Commercial in Confidence

Issue Date:  26 August 2022

Appendix A: Requirements & Proponents Response Template	3

1.	Prepay Meter Solution	3

1.1	Core Functions	3

2.	Metrology	5

2.1	Core Functions	5

2.2	Meter Configuration Options	7

2.3	External Interfaces	7

2.4	Delivery	8

2.5	Reference Sites	8

2.6	Technology Roadmap	8

3.	Vending Services	9

3.1	Core requirements for Prepayment solutions	9

3.2	Specific Requirements	11

3.3	Vending Technology Requirements	13

- Appendix A: Requirements & Proponents Response Template

Prepay Meter Solution

  - Core Functions

|  | Requirement | Background | Compliance / Alternatives |
| --- | --- | --- | --- |
| A.COR.BRQ.01 | Meter Admin: the set up and ongoing management of meters, reconciliation with field installation details, meter configuration changes and retailer record maintenance. | Meter details will be provided on a singular or batch process and will require ongoing management of configuration details, current retailer record following installation activity. Confirmation of physical site commissioning is also required and reconciliation with field installation records on a regular basis. |  |
| A.COR.BRQ.02 | Regular or Ad hoc Meter Register Reading: the reading of one or more meters in a predetermined schedule provided by a retailer to collect register(s) data using optical port or manual reading by field agent. | These readings will be used for billing when the prepay meter is in postpay mode or for annual reconciliation for prepay mode and also when site visit is carried out for faults or investigation. |  |
| A.COR.BRQ.03 | Tariff update: the meter can switch to an appropriate tariff table and updated rates as enforced via the vending token keyed into the meter. | Retailer can change the tariff structure of the prepay meter or update pricing rate anytime with notice to customers and this should be able to be implemented on the meter when the customer requests for the next immediate vending code after the change is done in PMS. |  |
| A.COR.BRQ.04 | Display: the meter can present current load, current credit balance in dollars and equivalent days, whether it is on emergency credit threshold already, days to disconnect warning and disconnection alerts either with sound or flashing message. The displayed information on the meter can also be relayed and presented using compatible in-home display. | Customers need to know current situation and be warned and alerted of impending disconnection. |  |
| A.COR.BRQ.05 | Configuration Update: the meter can be updated on non-disconnection windows and other settings such as emergency credit threshold and others via entry of the customer's next token since the change has been implemented in the PMS. | Retailer may wish to extend or shorten non-disconnection window for its customers and should be able to implement this without site visit by via token |  |

Metrology

  - Core Functions

|  | Requirement | Compliance / Alternatives |
| --- | --- | --- |
| MET.BRQ.01 | Max Physical Size 200x130x80mm (1 phase) 260x174x80mm (3 phase) Include as an attachment, layout drawings of all meters proposed showing dimensions |  |
| MET.BRQ.02 | Min Current 80 Amps (1 phase) 100 Amps (3 phase Whole Current) |  |
| MET.BRQ.03 | Min Diameter of Terminals 8.2mm (1 phase), 8.5mm (3 phase Whole Current) |  |
| MET.BRQ.04 | Terminal configuration 2 screws, slotted head combi BS5685 (1 phase) DIN43857 (3 phase) |  |
| MET.BRQ.05 | Operating Voltage 230VAC +/- 15% (1 phase) 400VAC +/- 15% (3 phase) |  |
| MET.BRQ.06 | Environmental Protection IP53 |  |
| MET.BRQ.07 | Accuracy of measurement elements Class 2 (1 phase) Class 1 (3 phase) – preferred |  |
| MET.BRQ.08 | International Standards IEC62052 Pt 11 and 21 IEC62053 Pt 23, or ANSI C12.19 |  |
| MET.BRQ.09 | Protocols AMS DLMS SML |  |
| MET.BRQ.10 | Immunity to Harmonics/Voltage spikes |  |
| MET.BRQ.11 | Measurement Quantities - kWh, kW, VArh, VAr import/ export/net, (4 quadrant metering), - V, I |  |
| MET.BRQ.12 | Pulse output DIN 43864 or IEC6253-31 |  |
| MET.BRQ.13 | Indicators Pulsing LED for consumption |  |
| MET.BRQ.14 | Meter Visual Display Display kW kWh (last account) Tariff Meter status (disconnected, tamper) Retailer and telephone number Communications signal strength for wireless communications (optional) Pre-pay (credit? other) Alphanumeric messaging |  |
| MET.BRQ.15 | Operating Temperature Minus 20 to plus 50 degrees C |  |
| MET.BRQ.16 | Labelling Asset number, bar code (to EAN Standard EAN 128), logo |  |
| MET.BRQ.17 | Power Consumption Normal continuous power consumption for steady-state metering with communications in stand-by mode |  |
| MET.BRQ.18 | Standard Warranty term offered (years) |  |
| MET.BRQ.19 | Meter life – minimum 15 years |  |
| MET.BRQ.20 | Meter support – minimum 15 years |  |

  - Meter Configuration Options

Core Functions

The following options have been identified as essential (E), desirable (D) of interest (I).  The Proponent should clearly indicate whether the functionality is currently in commercial production, is being developed, could be developed or not available.  If the particular function is being developed, please indicate when the function will be available.

|  | Requirement | Importance | Compliance / Alternatives |
| --- | --- | --- | --- |
|  | Supply Disconnect / Reconnect |  |  |
| MCO.BRQ.01 | Single phase Disconnect/Reconnect - switch 100 amps | E |  |
| MCO.BRQ.02 | Three Phase Disconnect/Reconnect - switch 100 amps across all 3 phases (whole current) | E |  |
|  | Load Limiting |  |  |
| MCO.BRQ.03 | Load Limiting – load switches a metered source off at remotely configured pre-set limit, manually re-set. | D |  |
|  | Other |  |  |
| MCO.BRQ.04 | Neutral fault detection | I |  |

  - External Interfaces

|  | Requirement | Compliance / Alternatives |
| --- | --- | --- |
| EXI.BRQ.01 | External field contractors: Is there provision for field contractors to verify meter installations? |  |
| EXI.BRQ.02 | Partnering: Provide details of any partnering arrangements with local systems integrators on similar projects |  |

  - Delivery

|  | Product Delivery |  |
| --- | --- | --- |
| DEL.BRQ.01 | Advise delivery date from receipt of order for Meter components sufficient to build, commission and to operate the Meter Network commercially |  |
| DEL.BRQ.02 | Flexibility to respond to “just in time” request for orders, to reconfigure meters in stock before shipment. |  |

  - Reference Sites

|  | References |  |
| --- | --- | --- |
| REF.BRQ.01 | List 3 reference sites where the PUB can visit to view the Prepay Meter technology being offered in commercial operation. Name of Client that has deployed technology and a brief description of the circumstances/drivers/market design Date when meters installed Volume installed Communications technology utilised, if applicable. Failure rate Summary of business KPIs since deployment |  |

  - Technology Roadmap

|  | Roadmap |  |
| --- | --- | --- |
| TRM.BRQ.01 | Set out the temporal roadmap for the ongoing development of the Meter technology |  |

Vending Services

  - Core requirements for Prepay Meter solutions

For each question, proponents are requested to specify whether their solution meets the functionality that is required. In response to each question, please indicate in the space provided:

| F (Full) | The solution meets 100% of the functionality requested and can be implemented now. |
| --- | --- |
| P (Partial) | The solution is partially compliant with the requirement and would need additional work to bring it to 100% functional. |
| NR (No but in Roadmap) | The current solution is not compliant with this requirement but is in the roadmap for delivery within the next 3 years |
| N (No) | The solution is not compliant with this requirement and it cannot be implemented. |

| Vending Channel and Vending System Business Requirements |  | Response (F/P/NR/N) | Response Detail |
| --- | --- | --- | --- |
| Vending Channel |  |  |  |
| Core.BRQ.01 | Ability to provide an extensive network of accessible prepay vending merchants across Kiribati that complies with international standards on secure financial transactions. |  |  |
| Core.BRQ.02 | Ability to provide electronic vending channels such as mobile-wallet, SMS and web vending that complies with international standards on secure electronic financial transactions. |  |  |
| Core.BRQ.03 | Provide a mechanism where it is simple for any person to top-up the desired account: - Confirmation of successful payment to the party making the payment and the account holder |  |  |
| Core.BRQ.04 | Channels must be available to customers to purchase and apply top-up credit to their accounts 24/7 |  |  |
| Core.BRQ.05 | Customers will always have two top-up channels available to them. This allows the customer to be always able to top-up in the event that the one of the channels are unavailable e.g. if the mobile or merchant network is down, customers can still top-up through the call centre or through an IVR channel |  |  |
| Core.BRQ.06 | There will be incentives for customers to top-up through channels with a cheaper cost to serve for the PUB |  |  |
| Core.BRQ.07 | Minimum and maximum limits for customer top-ups must be adjustable |  |  |
| Core.BRQ.08 | Top-up incentives must be configurable by channel and amount |  |  |
| Core.BRQ.09 | Security of information and systems is to adhere to all the PUB standards and policies |  |  |
| Vending System |  |  |  |
| Core.BRQ.10 | Ability to securely receive financial transactions from PoS (merchant or electronic vending), log the transaction and transmit to bank/clearing house. |  |  |
| Core.BRQ.11 | Ability to configure rules and messages for approved/declined transactions. Rules such as “Transaction Types allowed per Vending Channel and authorisation level (e.g. Standard, Goodwill)” Note: Goodwill is different from Emergency Credit. Emergency Credit is applied and governed by the rules in the Prepayment Management system which is an allowed “IOU” for the customer while Goodwill transaction is a straight free vending transaction generated by the PUB to the customer for some valid reason. This will typically just be allowed for Web vending using a PUB supervisor ID. |  |  |
| Core.BRQ.12 | Ability to ensure financial transaction is cleared prior to sending transaction request to the Prepayment Management System |  |  |
| Core.BRQ.13 | Ability to have secure interface with the following: Vending Channels Banks/ Financial Clearing House Prepayment Management System of the PUB |  |  |
| Core.BRQ.14 | Ability to offer Offshore remittance vending service against identified electricity meter |  |  |
| Core.BRQ15 | Ability to generate reports such as: Failed Top-ups by Meter Numbers Vending trend reports by amount, by frequency, by merchant location, by vending channel, by time Ad hoc reporting |  |  |

  - Specific Requirements

The prepay meter manages the decrementation of $credit within the meter as electricity is being consumed. The meter itself will enforce the automatic disconnection when the zero or negative credit (e.g. emergency credit) has been consumed. The meter likewise automatically reconnects supply once credit top-up via STS token is entered into the meter. There are certain rules for non-disconnection windows (such as weekends and holidays that are configured in the meter based on the PUB’s business rules). Therefore, a key requirement for the vending channel and vending system is the ability to receive payment and provide the prepay token to the customer. The meter itself provides information on remaining credit.

| Vending Channel and Vending System Business Requirements |  | Response (F/P/NR/N) | Response Detail |
| --- | --- | --- | --- |
| Vending Channel |  |  |  |
| A.BRQ.01 | For the prepay solution, customers will be able to purchase prepay credit top-up and receive prepay token equivalent to the amount purchased. |  |  |
| A.BRQ.02 | For the prepay solution, the customer will be informed of any promotions provided by the PUB (e.g. extra goodwill credit given to customers). |  |  |
| A.BRQ.03 | For the prepay solution, the customer will be informed of any error or warning message received from the prepayment management system in the event of system fault and inability to dispense prepay token. Back-up procedure for the Vending channel to divert customers to BCP channel (e.g. contact the PUB directly). |  |  |
| Vending System |  |  |  |
| A.BRQ.04 | For the prepay solution, ability to send transaction request to the Prepayment Management System and receive prepay token and message result from the Prepayment management system and send to the POS and electronic vending channel. |  |  |
| A.BRQ.05 | For the A prepay solution, ability to report on all vending transactions and send to the PUB including audit trail information: Channel Type (Merchant, Web, SMS, m-wallet) Merchant ID User ID Meter Number Transaction Date/Time Transaction Type (Standard, Goodwill) Transaction Amount Token Payment Type (cash, eftpos, credit card, etc) Message |  |  |

  - Vending Technology Requirements

The PUB requires information about the technology platform(s) on which the solution will be delivered. For areas where this is delivered “as a service” a high-level overview of the technologies will be sufficient.

For each question, proponents are requested to specify whether their solution meets the functionality that is required. In response to each question, please indicate in the space provided:

| CC (Currently Capable) | Current capability to deliver this solution/ service to existing clients. |
| --- | --- |
| FC (Future Capability) | Future capability to deliver this solution/ service is in the roadmap. |
| CO (Capability Out of Scope) | Capability to deliver this solution/ service is out of scope of the proponent’s response. |

Technology Description

For any infrastructure required to be supported by the PUB, please describe the technology on which the individual components based.

| Requirement |  | Response (CC/FC/CO) | Response Detail |
| --- | --- | --- | --- |
| TRQ.01 | What technology set is required or supports the solution? Please list the technology stack. |  |  |
| TRQ .02 | Is there any additional third-party software required to deploy the solution? Please list additional software requirements. |  |  |
| TRQ.03 | Is the solution based on a flexible architecture? Please provide range of technology that can be used to support the solution (e.g. DB server can be MS SQL or Oracle 10, 11g, etc) |  |  |
| TRQ.04 | Is the solution designed for high availability? |  |  |
| TRQ.05 | Please provide an architectural diagram of the proposed solution. |  |  |
| TRQ.06 | Please provide high level data architecture and data models. |  |  |
| TRQ.07 | Please describe the available and preferred data integration technologies. |  |  |
| TRQ.08 | Has this solution been deployed with other clients? |  |  |
| TRQ.09 | Please describe the integration approach with the PUB business & systems. |  |  |
| TRQ.10 | Please describe how robustness and reliability of interfaces are achieved. |  |  |
| TRQ.11 | Describe system’s reporting capabilities (scheduled, ad hoc)? |  |  |
| TRQ.12 | Describe the system's data exporting capabilities (scheduled, ad hoc)? |  |  |
| TRQ.12 | Describe the system's User Interface? (e.g. user preference setting, web based, etc) |  |  |
| TRQ.13 | Which security standards does your system comply with? Please list them. |  |  |
| TRQ.14 | Please describe the system’s user access security management. |  |  |
| TRQ.15 | Please describe how data access security is achieved. |  |  |
| TRQ.16 | Are there several layers of security enforced in the system, please describe the security layers. |  |  |
| TRQ.17 | Please describe system monitoring, management and administration. |  |  |
| TRQ.18 | Can an external system monitoring tool access the system log for integration with the central monitoring system? |  |  |
| TRQ.19 | How is the system version managed and maintained? |  |  |
| TRQ.20 | How is system availability and SLA compliance monitored and managed? |  |  |
| TRQ.21 | How long and frequent is the system’s maintenance window required for? |  |  |
| TRQ.22 | Is there any dependency on a third party to provide support/maintenance? |  |  |
| TRQ.23 | Please describe your minor and major patch and release cycles. |  |  |
| TRQ.24 | When is your next release schedule? |  |  |
| TRQ.25 | How are enhancements included for the next release inclusion? |  |  |
| TRQ.26 | Please describe back-up and restore procedures of your solution. |  |  |
| TRQ.27 | Please describe disaster recovery and business continuity procedures of your solution. |  |  |
| TRQ.28 | Please describe the typical performance level of your solution in terms of processing throughputs and response times. Please provide context in terms of the number of installation records being processed. |  |  |
| TRQ.29 | For a licensed the PUB owned arrangement, please list all the hardware required to deploy the solution. |  |  |
| TRQ.30 | Describe ability to comply with STS interface protocol for managing prepay tokens. |  |  |