## Sheet2
The discharge of LPG from an ISO Tank container to cylinders involves a specialized transfer system designed to safely move liquefied gas under pressure. The process generally requires components for vapor recovery to maintain pressure differentials and liquid transfer to move the product.
Here are the main parts of an LPG ISO tank discharge-to-cylinder system, categorized by their function:
1. ISO Tank Container (Source)
Pressure Vessel: The main stainless steel tank (typically 20ft) designed for pressurized LPG storage.
Bottom Discharge Valve (Liquid Valve): Located at the bottom, this is used to withdraw liquid LPG.
Airline Valve (Vapor Valve): Located at the top, used to inject or withdraw vapor to manage tank pressure.
Safety Relief Valve: Prevents over-pressurization.
Pressure Gauge: Monitors the internal pressure of the ISO tank.
Level Gauge (Magnetic/Rotary): Measures the liquid level.
Manhole Cover: Access point for inspection.
2. Transfer System and Piping
Liquid Transfer Hose (High-Pressure): Flexible, reinforced hose for transferring liquid LPG.
Vapor Return Hose: Connects the cylinder/storage bank to the ISO tank to return vapor, maintaining pressure equilibrium.
LPG Transfer Pump: Usually a sliding vane or centrifugal pump used to move liquid LPG.
Vapor Compressor: Used to move vapor from the cylinder bank back to the ISO tank, which boosts efficiency.
Ball Valves/Isolation Valves: Quarter-turn valves used to open/close the flow.
Emergency Shut-off Valves (ESV): Automatically close in case of fire or leaks.
Check Valves (Non-Return Valves): Ensure one-way flow, preventing backflow into the ISO tank.
Hydrostatic Relief Valves: Installed between two closed valves to protect piping from overpressure due to liquid expansion.
3. Cylinder Filling Station (Destination)
Filling Manifold: A piped header system that connects multiple cylinders to the supply hose.
Cylinder Filling Valves: Specific valves on the manifold for controlling individual cylinder fill.
LPG Filling Scales: Weighs cylinders during filling to prevent overfilling (usually equipped with auto-shutoff).
Fill Adapter/Couplings: Connects the hose to the cylinder valve (e.g., POL, Acme, or specialized quick-connectors).
4. Safety and Control Components
Grounding/Earthing Cable: Removes static electricity during transfer.
Emergency Shutdown System (ESD): A system to immediately halt operation in an emergency.
Gas Detectors: Sensors installed in the area to detect leaks.
Spill Pan: Placed under the discharge connection to catch minor leaks.
These components together ensure that liquid LPG is moved from the ISO tank, while vapor is balanced to keep the system safe and efficient.