REQUEST FOR QUOTATION
SPECIFICATION OF STANDARD GOODS

Procurement No: 54-G001-26

Specification

Background

Bonriki International Airport is the main international airport serving the Republic of Kiribati. The Airport Kiribati Authority is responsible for maintaining safe and reliable airfield infrastructure to support aircraft operations.

As part of the airport safety and infrastructure improvement program, the Airport Kiribati Authority intends to procure and install a modern Airfield Runway Lighting System to enhance visibility during night operations and low-visibility conditions. The project aims to improve operational safety and ensure compliance with international aviation standards.

All equipment supplied under this procurement must meet internationally recognized aviation standards and must be suitable for operation in a tropical coastal environment.

Runway (09/27) Cable LED Lighting System – Bonriki Airport (2011 m)

1. Applicable Standard

All lighting components, spacing, and control requirements must comply with ICAO Annex 14, Volume I – Aerodrome Design and Operations for runways licensed for night use, including edge, threshold, and end lighting.

2. Runway Overview

- Runway: 09/27

- Length: 2 011 m (6 598 ft)

- Surface: Asphalt

- Current Lighting:  A704 Solar RWY light (cable lighting system required)

3. Minimum Required LED Lighting Components

3.1 Runway Edge Lights

Purpose: Define runway lateral limits for night operations. 
Requirements:

- Type: High-intensity LED runway edge lights with photometric performance compliant with ICAO Annex 14 standards.

- Color: White (amber optional for last 600 m caution zone if required).

- Spacing: ≤ 60 m maximum between adjacent lights along each side of the runway for instrument runway guidance.

- Mounting: On frangible bases to reduce hazard if struck by aircraft.

- Quantity: Approx. 35 lights per side for 2 011 m runway (subject to final detailed design).

3.2 Runway Threshold Lights

Purpose: Mark threshold transition where landing begins. 
Requirements:

- Color: Green (facing approach); Red (facing departure direction).

- Placement: In a line perpendicular to runway centerline, ≤ 3 m outside runway edge.

- Quantity: Minimum 12 lights per threshold (6 green + 6 red).

3.3 Runway End Lights

Purpose: Mark the runway end for departing aircraft. 
Requirements:

- Color: Red unidirectional lights visible in runway use direction.

- Placement: In a line at right angles to runway axis ≤ 3 m outside runway end.

- Quantity: Minimum 12 lights per runway end (6 on each side of centerline).

3.4 Runway End Identifier Lights (REIL) — LED

Purpose: Improve threshold conspicuity and visual acquisition during approach. 
Requirements:

- Two high-intensity flashing white LED lights at each threshold (one on each side).

- Controlled by runway lighting control (tower/ground operations).

4. Optional / Recommended Additions for Enhanced Safety

These are not mandatory for basic night ops but recommended for improved situational awareness and IFR capability:

4.1 Approach Lighting System (ALS)

- A run of LED lights extending beyond threshold on extended runway centerline (e.g., 150–300 m).

- Offers a visual cue in moderate visibility conditions.

4.2 Touchdown Zone LED Lights

- Installed from threshold up to ~900 m to highlight touchdown zone.

- Typically required for precision runways (not currently required at Bonriki).

5. Power, Control & Protection Requirements

5.1 Power Distribution & Cabling

- Underground armored power cables: Sized for total LED load.

- Protective conduits and tracer tapes in trenches.

- Cable joints in accessible junction boxes with rated IP protection.

5.2 Constant Current Regulator (CCR)

- Multi-circuit CCR controlling runway lamp intensity and status.

- Adjustable lighting intensity (multiple steps) per prevailing conditions.

- Interfaces with control panel and monitoring system. 
“Note: The existing Constant Current Regulator (CCR) is currently dedicated to the PAPI lighting system. Assessment is required to determine whether it can safely support both the PAPI and the runway lighting systems.”

5.3 Control & Monitoring

- Central control station in ATC/operations room controlling:

  - Intensity levels

  - CIRCUIT status indications

  - Fault alarms and reporting

- Optional pilot-controlled lighting (ARCAL/PAL) for remote/night operations.

5.4 Surge, Earthing & Lightning Protection

- Surge protection for all lighting circuits and CCR input.

- Proper earthing and bonding per electrical safety standards.

6. Mounting & Civil Installation

- Frangible mounting bases on LED lights per ICAO Annex 14 requirements.

- Cable trenches and ducts must be installed under/adjacent to pavement without compromising runway structural integrity.

- Trenches must be reinstated and compacted per airport engineering standards.

7. Serviceability Standards

- Lighting system must have maintenance objectives, ensuring continuous guidance.

- Operators must report unserviceable lights so corrective action/NOTAMs can be issued.

8. Procurement-Ready Bill of Quantities (Estimates)

Summary of Required System Features

- Edge, threshold, and runway end LED lighting compliant with ICAO standard for night operations.

- Cable-fed LED lights with CCR control and monitoring.

- Frangible mountings and underground protected cabling.

- Optional advanced aids (ALS, centreline, touchdown zone) for IFR enhancements.

Installation services

The supplier shall provide full installation and commissioning services for the runway lighting system.

Installation services shall include:

• Site inspection and preparation if required
• Installation of runway lighting fixtures and related electrical components
• Installation of mounting bases and wiring systems
• Integration with the existing airfield lighting control system (if applicable)
• System testing and commissioning
• Operational testing to ensure compliance with aviation lighting requirements
• Provision of installation documentation and test reports

The supplier shall also provide training to airport maintenance personnel on operation and maintenance of the runway lighting system.

Delivery Time

The supplier must deliver and install the equipment within the period agreed in the contract. The preferred delivery and installation period is within 8 to 12 weeks after contract signing unless otherwise agreed.

Description of the Goods

Here, list all items to be Tendered

(This part may be replaced by a proprietary Supplier description)

Description of the Goods

The goods to be supplied under this procurement may include, but are not limited to, the following items:

| Item | Specification | Estimated Qty |
| --- | --- | --- |
| LED runway edge lights | High-intensity, ICAO compliant | ~140 (70 per side) |
| LED threshold lights (green/red) | ICAO compliant | 24 |
| LED runway end lights (red) | ICAO compliant | 24 |
| LED REIL units | Flashing white | 4 |
| CCR system with control panel | Multi-circuit | 1 |
| Isolating transformers | Depends on system design | As required |
| Armored power cable | Underground | ~6 000 m |
| Control cable | Shielded | ~6 000 m |
| Conduits & warning tape | Trench protection | ~6 000 m |
| Surge protectors | For all circuits | As required |
| Frangible bases | All lights | ~150 |

All equipment must comply with applicable international aviation standards and must be designed for continuous operation in airport environments.

Suppliers may provide detailed proprietary product descriptions and technical documentation for the proposed equipment.